## Flow_Diagram
Flow Diagram
Neuron
Gateway
FabNo
Machine_detail_1
Machine_detail_2
Energy Meter
(Energy Meter selection)
PTC
FabNo
IMEI No
Machine_detail_2
Machine_detail_1
Sending Configuration files
1.Modbus.cfg
2.tag_parser.json
1
2
3
Assembly Line Registration confirmation
4
PTC
CCS
CRM
Sending Air~Alert Registered information to CCS (fabNo)
Requesting the Compressor data
Sending compressor data to PTC
Sending Air~Alert Registered information to CRM (fabNo)
5
6
7
CCS will store this fabNo for further communication
CRM will store this fabNo for further communication

## Test Case 1
Test Case ID |  | T001 | Test Case Description | Assembly Line - Device Registration
Created By |  | Babu | Reviewed By |  |  | Version
QA Tester’s Log |  | Device Registration Test case creation
Tester's Name |  |  | Date Tested |  |  | Test Case (Pass/Fail/Not Executed)
S # | Prerequisites: |  |  | S # | Test Data
1 | Please refer the sheet "Prerequisite" |  |  | 1 | Machine Varient (EPSAC/AB/OFSAC) (Refer "TestData" - INPUT column for more details)
2 | Access to the below URL |  |  | 2 | Machine Type(C/CV20/CV40/CD/CVD/OA/OW/OLW) (Refer "TestData" - INPUT column for more details)
3 | https://elgi-prod.cloud.thingworx.com/Thingworx/Runtime/index.html?mashup=ELGi.COMP.RegisteredDevices.MU |  |  | 3 | Neuron Type (N3/N4) (Refer "TestData" - INPUT column for more details)
4 |  |  |  | 4
5 |  |  |  | 5
Test Scenario | Verify on device registration process
S # | Step Details |  | Action items | Expected Results |  |  | Actual Results | Pass / Fail / Not executed / Suspended
1 (Flow No:1,2,3) | Connect Gateway to Neuron (At Gateway End) |  | 1. Fetch FabNo,Machine_detail_1 and ,Machine_detail_2 from Neuron 2. Send FabNo,Imeino,Machine_detail_1 and ,Machine_detail_2 to PTC 3. Receive the modbus.cfg and tag_parser.json file based on Machine_detail_1 and Machine_detail_2 | Refer the "Prerequiste" sheet and sl no from 7 to 10
2 (Flow No:1,2,3) | Receive the device registration request from Gateway (At Platfrom End) |  | 1. Create Remote_thing 2. Create Local_thing and add shapes based on the Machine_detail_1 and Machine_detail_2 3. Share the modbus.cfg and tag_parser.json to Gateway 4. Share the FabNo to CRM/CCS | Refer the "TestDate" sheet column "OUTPUT" and it is matching with Registered Device - Confirmation screen
3 (Flow No:4) | Registration confirmation |  | 1. Log-in to Device_Registration UI as a Assembly_user 2. Confirm the device get registred | Refer the "TestDate" sheet column "OUTPUT" and it is matching with Registered Device - Confirmation screen
4 (Flow No:6) | Collecting Compressor meta data from CCS (At Platform end) |  | 1. Request Compressor meta data from CCS 2. Update the compressor meta data at Thing level | Refer the "NamePlate Details " of the compressor The below property should be updated in the Registered Device - Confirmation screen Property to updated : Machine_varient Rated_Power Rated_Pressure Rated_CFM Operating_Voltage Operating_Frequency TPL_NO
5 (Flow No:5,7) | Sending AirAlert Registred Information to CRM/CCS |  | 1. Sending FabNo to CRM/CCS | Verify in CRM/CCS System whether the given fabNo received at IT end
Note
1. Future Expansion - Energy meter with EPSAC/AB/OFSAC
2. Future Expansion - RTD/BTD/Vibration with OFSAC

## Prerequisite
Device Registration
Prerequisite
S.No | Task
1 | Activate the SIM Card provided with the Gateway
2 | Update the FAB Number in Neuron.
3 | Insert the Activated SIM Card inside Gateway
4 | Connect the Gateway to Neuron with the Wiring Harness
5 | Power Reset both Neuron and Gateway.
6 | Check LED Status: 1) Signal Strength Multi color LED (D1) 2) SIM LED (D2) 3) Modem GSM LED(D3) 4) RS-485/Modbus Communication LED (D4) 5) Power LED (D5) 6) WIFI LED (D6)
7 | Make sure Power LED glows which indicates that the module is Powered on
8 | SIM LED(D2) will glow within couple of minutes after powered on. If it glows then we can make sure that SIM Card is inserted properly and detected by the module. If not, Kindly recheck proper insertion of SIM Card and Power Reset the Gateway
9 | If the Multi Color LED show green after proper installation, Signal Strength is good and it will start the data connection(Modem GSM LED(D3) will start blinking), if it shows red, then it seems GSM Signal is weak
10 | Once the application inside Gateway starts, RS-485/Modbus Communication LED (D4) will start blinking
11 | If GSM Signal Strength is weak and want to use Ethernet, connect Open Ethernet Cable for Ethernet communication and Power Reset the Gateway
12 | If GSM Signal Strength is weak and want to use WIFI, set WIFI username as TestELGi and password as TestELGi in Hotspot, then Power Reset the Gateway. WIFI signal strength can be monitored via Multi-color LED (D1).
Registered Device - Confirmation screen
URL | https://elgi-prod.cloud.thingworx.com/Thingworx/Runtime/index.html?mashup=ELGi.COMP.RegisteredDevices.MU
UserName
Password
Screen
Failure Logs
Url | https://elgi-prod.cloud.thingworx.com/Thingworx/Runtime/index.html?mashup=ELGI.COMP.AgentRegistrationFailure.MU

## TestData
Machine Category |  |  |  |  | INPUT | [7 empty] | OUTPUT
Machine Group | Neuron_version | Varient | Machine_details_1 | Machine_details_2 | Neuron_Setting | [7 empty] | Device Registration - Confirmation Screen
[5 empty] | SumPressure | VFD | Winding | Dryer | OA | OLW | OW | FabNo | ThingName | TemplateName | Shapes
EPSAC | N3 | N3_EPSAC_C | 4160 | 0 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC
|  | N3_EPSAC_C_Sump |  | 1 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.SumpPr.TS
|  | N3_EPSAC_CD |  | 8 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.Dryer.TS
|  | N3_EPSAC_CD_Sump |  | 9 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.SumpPr.TS,ELGi.comp.Dryer.TS
|  | N3_EPSAC_CV20 |  | 6 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.VFD_CV20.TS
|  | N3_EPSAC_CV20_Sump |  | 7 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.VFD_CV20.TS,ELGi.comp.SumpPr.TS
|  | N3_EPSAC_CV40 |  | 2 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS
|  | N3_EPSAC_CV40_Sump |  | 3 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.SumpPr.TS
|  | N3_EPSAC_CVD20 |  | 14 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.VFD_CV20.TS,ELGi.comp.Dryer.TS
|  | N3_EPSAC_CVD20_Sump |  | 15 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.VFD_CV20.TS,ELGi.comp.Dryer.TS,ELGi.comp.SumpPr.TS
|  | N3_EPSAC_CVD40 |  | 10 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.Dryer.TS
|  | N3_EPSAC_CVD40_Sump |  | 11 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.Dryer.TS,ELGi.comp.SumpPr.TS
| N4 | N4_EPSAC_C | 4224 | 0 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC
|  | N4_EPSAC_C_Sump |  | 1 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.SumpPr.TS
|  | N4_EPSAC_CD |  | 8 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.Dryer.TS
|  | N4_EPSAC_CD_Sump |  | 9 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.SumpPr.TS,ELGi.comp.Dryer.TS
|  | N4_EPSAC_CV20 |  | 6 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.VFD_CV20.TS
|  | N4_EPSAC_CV20_Sump |  | 7 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.VFD_CV20.TS,ELGi.comp.SumpPr.TS
|  | N4_EPSAC_CV40 |  | 2 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS
|  | N4_EPSAC_CV40_Sump |  | 3 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.SumpPr.TS
|  | N4_EPSAC_CVD20 |  | 14 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.VFD_CV20.TS,ELGi.comp.Dryer.TS
|  | N4_EPSAC_CVD20_Sump |  | 15 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.VFD_CV20.TS,ELGi.comp.Dryer.TS,ELGi.comp.SumpPr.TS
|  | N4_EPSAC_CVD40 |  | 10 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.Dryer.TS
|  | N4_EPSAC_CVD40_Sump |  | 11 |  |  |  |  | NA | NA | NA |  | FabNo | EPSAC | ELGi.comp.VFD.TS,ELGi.comp.Dryer.TS,ELGi.comp.SumpPr.TS
AB | N3 | N3_AB_C_Sump | 8256 | 1 |  |  |  | NA | NA | NA | NA |  | FabNo | AB | ELGi.comp.SumpPr.TS,ELGi.comp.ABSeriesParameters.TS
|  | N3_AB_CV20_Sump |  | 7 |  |  |  | NA | NA | NA | NA |  | FabNo | AB | ELGi.comp.VFD.TS,ELGi.comp.VFD_CV20.TS,ELGi.comp.SumpPr.TS,ELGi.comp.ABSeriesParameters.TS
|  | N3_AB_CV40_Sump |  | 3 |  |  |  | NA | NA | NA | NA |  | FabNo | AB | ELGi.comp.VFD.TS,ELGi.comp.SumpPr.TS,ELGi.comp.ABSeriesParameters.TS
| N4 | N4_AB_C_Sump | 8320 | 1 |  |  |  | NA | NA | NA | NA |  | FabNo | AB | ELGi.comp.SumpPr.TS,ELGi.comp.ABSeriesParameters.TS
|  | N4_AB_CV20_Sump |  | 7 |  |  |  | NA | NA | NA | NA |  | FabNo | AB | ELGi.comp.VFD.TS,ELGi.comp.VFD_CV20.TS,ELGi.comp.SumpPr.TS,ELGi.comp.ABSeriesParameters.TS
|  | N4_AB_CV40_Sump |  | 3 |  |  |  | NA | NA | NA | NA |  | FabNo | AB | ELGi.comp.VFD.TS,ELGi.comp.SumpPr.TS,ELGi.comp.ABSeriesParameters.TS
OFSAC (OA) | N4 | N4_OFSAC_OA_C | 12928 | 1024 |  |  |  | NA |  |  |  |  | FabNo | OFSAC | ELGi.comp.DoubleStage.TS
|  | N4_OFSAC_OA_CV40 |  | 1026 |  |  |  | NA |  |  |  |  | FabNo | OFSAC | ELGi.comp.DoubleStage.TS,ELGi.comp.VFD.TS
OFSAC(OW) | N4 | N4_OFSAC_OLW_C | 13440 | 0 |  |  |  | NA |  |  |  |  | FabNo | OFSAC | ELGi.comp.WaterCooled.TS
|  | N4_OFSAC_OLW_CV40 |  | 2 |  |  |  | NA |  |  |  |  | FabNo | OFSAC | ELGi.comp.WaterCooled.TS,ELGi.comp.VFD.TS
|  | N4_OFSAC_OW_C |  | 1024 |  |  |  | NA |  |  |  |  | FabNo | OFSAC | ELGi.comp.WaterCooled.TS,ELGi.comp.DoubleStage.TS
|  | N4_OFSAC_OW_CV40 |  | 1026 |  |  |  | NA |  |  |  |  | FabNo | OFSAC | ELGi.comp.WaterCooled.TS,ELGi.comp.DoubleStage.TS,ELGi.comp.VFD.TS